## Sheet1
CHECK LIST FOR SERVICE STATIONS DISPENSING PETROL & LPG |  |  | DETAILS
Site Occupier details and Equipment Ownership Details
Oil Company details/ Gas Company details
OCCUPIER DETAILS
Company Name
Business Name
Workplace Address
Contact name
Position
Contact number
SITE MANAGER
Telephone number
Franchise agreement ( most common and generally for 10 years )
Dealer owned franchise( owns premises, 5year supply agreement )
Commission Agent agreement ( 30 days notice )
EQUIPMENT OWNERSHIP DETAILS ( Bullet, Dispensers, Fatboy, Workshop etc )
Organisation Name
Address
Contact name
Position
Telephone
D/G Registration details
Inspector
Date
CHECK LIST FOR SERVICE STATIONS DISPENSING PETROL & LPG
D/G STORAGE & HANDLING REGS. (2000) |  |  | COMMENTS/ RECOMMENDATIONS
CONSULTATION, |  | DG S&H Regs 401
INDUCTION, SUPERVISION AND TRAINING ACCEPTABLE |  | DG S&H Regs 402
HAVE THE HAZARDS BEEN IDENTIFIED |  | DG S&H Regs 404
HAVE RISK ASSESSMENTS BEEN CONDUCTED ON HAZARDS |  | DG S&H Regs 405
HAVE CONTROLS BEEN IMPLEMENTED TO CONTROL THE RISKS |  | DG S&H Regs 407
PPE SUITABLE, MAINTAINED, CLEAN AND SERVICEABLE |  | DG S&H Regs 411
VISITORS PROVIDED INFORMATION |  | DG S&H Regs 412
ADEQUATE SECURITY OF PREMISES |  | DG S&H Regs 413
DANGEROUS GOODS PROTECTED AGAINST IMPACT |  | DG S&H Regs 421
MEASURES TO CONTROL SPILLS AND LEAKS DURING TRANSFER |  | DG S&H Regs 423
MEASURES TO CONTROL STATIC ELECTRICITY DURING TRANSFER |  | DG S&H Regs 423
MEASURES TO CONTROL VAPOUR GENERATION DURING TRANSFER |  | DG S&H Regs 423
PLACARDING & SAFETY SIGNS ACCEPTABLE |  | DG S&H Regs 429
EMERGENCY MANAGEMENT PLAN / CONTACTS AVAILABLE |  | DG S&H Regs 437
SITE PLAN ACCEPTABLE |  | DG S&H Regs 427/28
SPILL CONTROL PLAN |  | DG S&H Regs 422
MANIFEST INFORMATION CORRECT |  | DG S&H Regs 427
CONTROL OF IGNITION SOURCES |  | DG S&H Regs 424
EQUIPMENT FOR CLEAN UP AVAILABLE |  | DG S&H Regs 435
ADEQUATE FIRE PROTECTION SYSTEM - ADEQUATELY INSTALLED, TESTED AND MAINTAINED |  | DG S&H Regs 435
REGISTER OF DANGEROUS GOODS |  | DG S&H Regs 442
EMERGENCY RESPONSE PLAN |  | DG S&H Regs 444
INCIDENT INVESTIGATION PROCEDURES |  | DG S&H Regs 445
IMPLEMENTATION OF CONTROLS ARISING FROM INCIDENTS |  | DG S&H Regs 446
NOTIFICATION GIVEN TO THE AUTHORITY OF DG STORAGE AND HANDLING |  | DG S&H Regs 506
SAFE WORK PROCEDURE PROVIDED BY MANAGEMENT |  | DG S&H Regs 405
AS/NZS 1940 (2004)- THE STORAGE AND HANDLING OF FLAMMABLE AND COMBUSTABLE LIQUIDS
ALL ELECTRIC'S SUITABLE FOR HAZ. ZONES |  | AS1940 - 3.3
NO SMOKING SIGNS DISPLAYED |  | AS1940 7.2.5 and 3.8.2
SMOKING IS PROHIBITED IN HAZARDOUS AREAS ( AS 2430 )
SAFETY INSTRUCTIONS ON DISPENSERS |  | AS1940 7.3.5
EMERGENCY STOPS CLEARLY MARKED |  | AS1940 7.2.4
CUSTOMER OPERATED NOZZLES ( no latching device ) |  | AS1940 7.4.2
FIRE EXTINGUISHER REQUIREMENTS |  | AS1940 11.7.1
BOLLARD PROTECTION OR KNOCK OVER VALVE |  | AS1940 8.2.4
FUEL DISPENSING GENERAL requirements |  | AS1940 7.2
SAFETY PROCEDURES FOR ALL ACTIVITIES |  | AS1940 7.6.2
VENT OUTLET LOCATION ( 4m above ground ) |  | AS1940 5.4.4
VENT TERMINAL (protection and flame arrester ) |  | AS1940 5.4.5
AS/NZS 1596 (2002) – THE STORAGE AND HANDLING OF LPG
DECANTING PROCEDURE |  | Appendix L
TO AN OPENING INTO A BUILDING 2 m. |  | AS 1596 7.4.3
TO A NEIGHBOURING PROPERTY OR COMBUSTIBLE MATERIALS 5m. |  | AS 1596 7.4.3
TO PUBLIC PLACES 3 m |  | AS 1596 7.4.3
TO D/G STORAGE TANK 3m |  | AS 1596 7.4.3
TO DISPENSERS OF ANY TYPE OF FUEL 3m. |  | AS 1596 7.4.3
TO A DRAIN, PIT OR BASEMENT 3m. |  | AS 1596 7.4.3
TO ANY STRUCTURE LIMITING EGRESS 2m. |  | AS 1596 7.4.3
TO ABOVE GROUND LPG BULLET 5m. |  | AS 1596 9.5.19
LOCKABLE DOME |  | AS 1596 3.4.1- 3.4.3
SAFETY VALVE ( protected from physical damage) |  | AS 1596 3.4.1- 3.4.3
FILLER VALVE ( primary shut down- check non return valve is working ) |  | AS 1596 3.3.4
FILLER VALVE ( manual shut off wheel or compound valve ) |  | AS 1596 3.3.5
FIXED LIQUID LEVEL GAUGE PROVIDED |  | AS 1596 3.5.4
PRESSURE GAUGE PROVIDED |  | AS 1596 3.5.5
PROVISION FOR EMPTYING TANK ( shut off valve and excess flow valve) |  | AS 1596 3.5.8
ELECTRICAL EQUIPMENT AND WIRING COMPLIES WITH AS 3000 |  | AS 1596 3.5.9
ABOVE GROUND LPG TANKS - SEPARATION DISTANCES( table 4.1 ) |  | AS 1596 4.2.1
8 KL LPG TANK TO PUBLIC PLACE > 6m |  | AS 1596 see table 4.1
8 KL LPG TANK TO PROTECTED PLACE > 10m |  | AS 1596 see table 4.1
8 KL LPG TANK TO FLAMMABLE LIQUIDS STORE > 6m |  | AS 1596 4.2.6
U/G STORAGE SYSTEMS- This section refers to tank location and anchoring
TANK TO ADJACENT TANK 1m |  | AS 1596 see table 5.1
TANK TO PUBLIC PLACE 3m |  | AS 1596 see table 5.1
TANK TO ADJACENT PROPERTY 6m |  | AS 1596 see table 5.1
TANK TO PROTECTED PLACE 6m |  | AS 1596 see table 5.1
STYLE "A" DISPENSER SYSTEM |  | AS 1596 9.3.2
EXCESS FLOW VALVE PROVIDED |  | AS 1596 9.3.2
REMOTE SHUT OFF VALVE PROVIDED |  | AS 1596 9.3.2
PIPE-SHEAR PROVISION PROVIDED |  | AS 1596 9.3.2
CONTROL VALVE INSIDE CABINET |  | AS 1596 9.3.2
MANUALLY OPERATED +VE SHUT OFF VALVE |  | AS 1596 9.3.2
EXCESS FLOW VALVE PROVIDED |  | AS 1596 9.3.2
OVERSPEED SENSOR PROVIDED |  | AS 1596 9.3.2
PUMP CONTROL (switch inside can shut down remote pump ) |  | AS 1596 9.3.2
TEST SHUT DOWN ( at the dispenser, let their operator activate button ) |  | AS 1596 9.3.2
DISPENSING HOSE( self sealing break away coupling ) |  | AS 1596 9.3.3
DISPENSING NOZZLE ( self sealing type ) |  | AS 1596 9.3.4
LATCHING DEVICE (prohibited) |  | AS 1596 9.3.4
ACME CAPS PROVIDED X2 ( check with attendant ) |  | AS 1596 9.3.5
ELBOW LENGTH THERMAL RESISTANT GLOVES (check with attendant) |  | AS 1596 10.9.5, 10.12.6
OPEN AND CLOSED POSITION OF VALVES CLEARLY MARKED |  | AS 1596 D1
EMERGENCY SHUT DOWN MARKED IN RED |  | AS 1596 D2.1
TANK PLACARD (24 hour phone number.) |  | AS 1596 D2.2, 2.3
EMERGENCY INFORMATION PANEL ( as per ADG Code ) |  | AS 1596 D2.2, 2.3
FLAMMABLE GAS, NO SMOKING |  | AS 1596 D2.3, 2.4
CYLINDER FILLING INSTRUCTIONS |  | AS 1596 D4
EMERGENCY PROCEDURES DISPLAYED |  | AS 1596 fig D1
REMOTE SHUT DOWN SYSTEM (RSDS ) X2 |  | AS 1596 9.5.14
IGNITION SOURCES IN HAZARDOUS AREA (as per AS 2430 ) |  | AS 1596 9.2.1
SAFETY MANAGEMENT SYSTEM ( LPG Auto Retail Outlets COP ) |  | AS 1596 9.8
OPERATING PROCEDURES
OPERATING PROCEDURES |  | AS 1596 10.3.4
MAINTENANCE PROCEDURES |  | AS 1596 10.3.5
EMERGENCY PROCEDURES |  | AS 1596 10.3.6
TRAINING PROCEDURES |  | AS 1596 10.3.7.1
CONTRACTOR PROCEDURES |  | AS 1596 10.3.7.2
SUPERVISION AND RECORDS |  | AS 1596 10.4.2 and 10.4.3
TESTING AND INSPECTION PROCEDURES |  | AS 1596 10.5.1- 10.5.12
NEW OR MODIFIED EQUIPMENT PROCEDURES |  | AS 1596 10.6.1
AS/NZS1200 (2000)- PRESSURE EQUIPMENT
TANK DESIGNED TO AS1200 - VIEW COMPLIANCE PLATE |  | AS1200- 2.1 and 2.2
DESIGN PRESSURE, CAPACITY IN CUBIC METRES. |  | AS1200 - table 2.1
MAINTENANCE ( 10 Year internal / 2 year external - Table 4.1 AS 3788 (2006) ) |  | AS3788- table 4.1 section 7
ROAD TRANSPORT REFORM (DG) REGS and ADG--- THIS SECTION NEEDS TO BE REVIEWED- the 7th edition will be available in Sept 2007!!!
This section applies to bulk gas and petrol tankers which may be unloading at the service station and the procedures the service station has to control the risks.
General requirements:
IS THERE A DESIGNATED AREA FOR VEHICLES TO TRANSFER DG |  | 10.2.3 ADG
PROCEDURE AVAILABLE TO ENSURE TWO TANKERS DO NOT UNLOAD AT THE SAME TIME
MAINTENANCE, INSPECTION AND TEST RECORDS FOR HOSE ASSEMBLY |  | 10.7(3)
IS THE VEHICAL ABLE TO DRIVE AWAY IN THE FORWARD DIRECTION |  | 10.2.1 ADG
CONTROL OF IGNITIAN SOURCES DURING TRANSFER |  | 10.3.1 ADG
If truck is unloading at time of audit
SHIPPING DOCUMENTATION AVAILABLE |  | 11.4
EMERGENCY INFORMATION AVAILABLE |  | 11.8
FIRE EXTINGUISHERS IN ACCORDANCE WITH TABLE 12.2 ADG |  | 12.3
NO IGNITIAN SOURCES ON VEHICLE |  | 13.6
DISTANCES REQUIRED FOR SEPARATION OF VEHICLE FROM IGNITION SOURCES: |  | 10.3.1 ADG
DRIVER AND VEHICLE LICENCED |  | 18.4
VEHICLE INSURED |  | 8.5
ENGINE STOPPED WHEN COUPLING |  | 10.3.2 ADG
TANK ELECTRICALLY BONDED |  | 10.3 ADG
PERSON TO REMAIN WITH VEHICLE DURING TRANSFER |  | 10.5.2 ADG
ADAQUATE LIGHT DURING TRANSFER |  | 10.5.4 ADG
WARNING SIGNS MOUNTED FRONT AND REAR OF VEHICLE (GAS) |  | 10.6.4 ADG
References:
The Dangerous Goods (Storage and Handling) Regulations 2000
AS 1940 The Storage and handling of flammable and combustible liquids
AS 1596 Storage and Handling of LPG
LPG Automotive Retail Outlets COP for safe operation
AS 3788 Pressure equipment-Inservice inspection
AS 2430: 1- 9 Classification of hazardous areas
Guidance notes - Testing of D/G Storage Tanks & circular 20 etc from VWA
Road Transport Reform (Dangerous Goods) Regulations and Australian Dangerous Goods Code
Note on H38: 401. Consultation with workers An occupier of premises where dangerous goods are stored and handled, must consult with persons engaged by the occupier to work at the premises whose health or safety is likely to be affected by the dangerous goods and any health and safety representative of those persons, regarding- (a) induction, training, information provision, hazard identification, risk assessment and risk control; and (b) any proposed changes to structures, plant, processes or systems of work that are likely to increase the risk to those persons.
Note on H39: 402. Induction, information, training and supervision (1) An occupier of premises where dangerous goods are stored and handled must ensure that a person involved with the storage and handling of dangerous goods at the premises and any health and safety representative of that person, is provided with induction, information, training and supervision that is- (a) in a language or manner appropriate to the person; and (b) relevant to the tasks undertaken and the risks associated with those tasks. (2) An occupier of premises where dangerous goods are stored and handled must ensure that the induction, information and training provided under sub-regulation (1) includes instruction in- (a) the nature of the hazards and properties of the dangerous goods and the processes used for the identification, assessment and control of the risks relevant to the person's duties; and (b) the purpose, use and maintenance of the measures for the control of those risks; and (c) the systems of work and the conduct of persons at the premises in so far as the systems of work and conduct of persons may affect safe storage and handling of dangerous goods; and (d) the operation of the emergency plan for the premises and any procedures and equipment that may be required for use in the event of an emergency; and (e) the proper use and fitting of personal protective equipment. (3) A record of induction and training activities carried out in accordance with this regulation must be made and kept for a minimum of 5 years.
Note on H40: 404. Identification of hazards (1) An occupier of premises where dangerous goods are stored and handled must ensure that any hazard associated with the storage and handling of dangerous goods at the premises is identified, having regard to the state of knowledge of the hazard. (2) Without affecting the generality of sub-regulation (1), the occupier, when identifying hazards, must have regard to- (a) any information about the hazardous properties inherent to the dangerous goods, including a MSDS for the dangerous goods available to the occupier; and (b) the chemical and physical properties of the dangerous goods, including physical state, viscosity, vapour pressure, chemical energy, particle size, solubility, electrical conductivity, reactivity, combustion products and concentration; and (c) any manufacturing and transport processes at the premises involving the dangerous goods, including the temperatures and pressures to which the goods are subjected, physical processes such as separation, mixing, absorption and changes of state and processes involving chemical reaction; and (d) the structures, plant (including the characteristics of the materials used in the plant), systems of work and activities that are used in the storage and handling of the dangerous goods at the premises; and (e) the physical location and arrangement of areas, structures and plant used for the storage and handling of the dangerous goods at the premises; and (f) the structures, plant (including the characteristics of the materials used in the plant), systems of work and activities that are not used to store or handle the dangerous goods at the premises but that could interact with the dangerous goods at the premises; and (g) the chemical and physical reaction between dangerous goods and other substances and articles with which the dangerous goods may come into contact at the premises; and (h) the type and characteristics of incidents associated with the dangerous goods, including incidents affecting the structures or plant used to store or handle the dangerous goods.
Note on H41: 405. Risk assessment (1) If a hazard is identified under regulation 404, an occupier of premises where dangerous goods are stored and handled must ensure that an assessment is made of the risks associated with the hazard. (2) Without limiting the generality of sub-regulation (1), the occupier, in conducting an assessment of risk, must have regard to the matters specified in regulation 404(2) so far as they relate to the storage and handling of dangerous goods at the premises. (3) The occupier must review the assessment- (a) if there is a significant change to any process or system of work in relation to the storage and handling of dangerous goods; and (b) if there is evidence to indicate that the risk assessment no longer adequately assesses the risk associated with any hazard; and (c) if required to do so under regulation 446 as a result of an incident occurring at the premises; and (d) at intervals of not more than 5 years from the assessment or last review. (4) The occupier must- (a) make a record of the assessment and any review of the assessment; and (b) keep a copy of that record while the assessment is current or being reviewed.
Note on H42: 407. General duty to control risk (1) An occupier of premises where dangerous goods are stored and handled must ensure that any risk associated with the storage and handling of dangerous goods at the premises- (a) is eliminated; or (b) if it is not practicable to eliminate the risk, is reduced so far as is practicable. (2) When complying with sub-regulation (1), the occupier must consider eliminating or reducing risk associated with the storage and handling of dangerous goods by- (a) substituting other goods, or other dangerous goods, that have a lower risk associated with their storage and handling; and (b) reducing the quantity of dangerous goods handled.
Note on H43: 411. Risk to workers (1) An occupier of premises where dangerous goods are stored and handled must not rely solely on administrative controls or personal protective equipment to eliminate or reduce risk to persons engaged by the occupier to work at the premises, unless it is not practicable to- (a) eliminate the use of dangerous goods or the risk associated with the use of dangerous goods; or (b) reduce the risk associated with the use of dangerous goods by- (i) the substitution of other dangerous goods that have a lower risk associated with their storage and handling; or (ii) the use of engineering controls; or (iii) isolation of the dangerous goods from persons. (2) If an occupier of premises where dangerous goods are stored and handled uses personal protective equipment to eliminate or reduce risk to persons engaged by the occupier to work at the premises, the occupier must- (a) provide personal protective equipment that is suitable for use with the dangerous goods; and (b) ensure that the personal protective equipment is maintained in a clean and serviceable condition. (3) A person must not wilfully damage or render ineffective any personal protective equipment provided under sub-regulation (2).
Note on H44: 412. Visitors to premises An occupier of premises where dangerous goods are stored and handled must ensure that a visitor to the premises is provided with information, safety instructions and supervision that are sufficient to ensure that any risk to the visitor or any other person on the premises that is associated with the storage and handling of dangerous goods is reduced so far as is practicable.
Note on H45: 413. Security at premises An occupier of premises where dangerous goods are stored and handled must, so far as is practicable, prevent access to the premises by unauthorised persons.
Note on H46: 421. Protection from impact An occupier of premises where dangerous goods are stored and handled must ensure that the dangerous goods and any structure or plant associated with the storage and handling of the dangerous goods is, so far as is practicable, protected against damage from impact with vehicles, mobile plant, ships or boats.
Note on H47: 423. Transfer of dangerous goods (1) An occupier of premises where dangerous goods are stored and handled must ensure that any risk associated with the transfer of dangerous goods- (a) from area to area within the premises; or (b) from or into a container on the premises- is eliminated, or if it is not practicable to eliminate the risk, is reduced so far as is practicable. (2) In controlling risk in accordance with sub-regulation (1), the occupier must, as relevant, have regard to- (a) the need for measures to- (i) control spills and leaks; and (ii) minimise static electricity; and (iii) control vapour generation; and (b) the compatibility of pipework at the premises. (3) In relation to the transfer of dangerous goods into a container used for the storage of dangerous goods in bulk, the occupier must ensure, so far as is practicable, that engineering controls are used to control the risk associated with over-filling the container.
Note on H48: 423. Transfer of dangerous goods (1) An occupier of premises where dangerous goods are stored and handled must ensure that any risk associated with the transfer of dangerous goods- (a) from area to area within the premises; or (b) from or into a container on the premises- is eliminated, or if it is not practicable to eliminate the risk, is reduced so far as is practicable. (2) In controlling risk in accordance with sub-regulation (1), the occupier must, as relevant, have regard to- (a) the need for measures to- (i) control spills and leaks; and (ii) minimise static electricity; and (iii) control vapour generation; and (b) the compatibility of pipework at the premises. (3) In relation to the transfer of dangerous goods into a container used for the storage of dangerous goods in bulk, the occupier must ensure, so far as is practicable, that engineering controls are used to control the risk associated with over-filling the container.
Note on H49: 423. Transfer of dangerous goods (1) An occupier of premises where dangerous goods are stored and handled must ensure that any risk associated with the transfer of dangerous goods- (a) from area to area within the premises; or (b) from or into a container on the premises- is eliminated, or if it is not practicable to eliminate the risk, is reduced so far as is practicable. (2) In controlling risk in accordance with sub-regulation (1), the occupier must, as relevant, have regard to- (a) the need for measures to- (i) control spills and leaks; and (ii) minimise static electricity; and (iii) control vapour generation; and (b) the compatibility of pipework at the premises. (3) In relation to the transfer of dangerous goods into a container used for the storage of dangerous goods in bulk, the occupier must ensure, so far as is practicable, that engineering controls are used to control the risk associated with over-filling the container.
Note on H50: 429. Outer warning placards If the quantities of dangerous goods stored and handled at premises exceed the relevant quantities specified in the column headed "Placarding Quantity" in the table in Schedule 2, the occupier of those premises must ensure that a "HAZCHEM" outer warning placard as specified in Schedule 4 is displayed- (a) in the case of a farm or a school, university or other educational institution, at the main road entrance to the premises; and (b) in the case of any other premises, at every entrance for road vehicles and every rail entrance.
Note on H51: 437. Planning for emergencies (1) This regulation applies in relation to premises where dangerous goods are stored and handled in quantities that exceed the relevant quantities specified in the column headed "Manifest Quantity" in the table in Schedule 2. (2) An occupier of premises to which this regulation applies must ensure that a written plan for dealing with any emergency associated with the storage and handling of dangerous goods on those premises is- (a) developed, implemented and maintained; and (b) communicated to- (i) persons who are engaged by the occupier to work at the premises and who may be exposed to risk as a result of an emergency; and (ii) persons in management and control of adjacent premises, if persons or property on the adjacent premises may be exposed to risk as a result of an emergency. (3) In developing or reviewing the emergency plan, the occupier must- (a) request the written advice of the emergency services authority; and (b) have regard to that written advice. (4) The occupier must ensure that the emergency plan required under this regulation reduces the risk, so far as is practicable, associated with an emergency. (5) Without limiting the generality of this regulation, the occupier must ensure that the plan clearly describes the location of the manifest maintained under Subdivision 1 of this Division. (6) The occupier must review the emergency plan- (a) if there is a change in circumstances at the premises and the plan no longer complies with sub-regulation (4); and (b) at intervals of not more than 5 years from the date on which the plan was developed or last reviewed.
Note on H52: 427. Manifest to be maintained (1) Premises where dangerous goods are stored and handled in quantities that exceed the relevant quantities specified in the column headed "Manifest Quantity" in the table in Schedule 2 are prescribed premises for the purposes of section 30 of the Act. (2) A manifest is in the prescribed form for the purposes of section 30 of the Act if it contains the information specified in Schedule 3. (3) An occupier of prescribed premises must ensure that the manifest is kept on the premises in a place where it is readily accessible to the emergency services authority. 428. Revision of manifest An occupier of premises referred to in regulation 427 must ensure that the manifest is revised as soon as possible after a change in any of the information specified in Schedule 3.
Note on H53: 422. Spill containment (1) An occupier of premises where dangerous goods are stored and handled must ensure that, in each area at the premises where dangerous goods are stored or handled, provision is made for spill containment that will- (a) eliminate the risk from any spill or leak of solid or liquid dangerous goods, or if it is not practicable to eliminate the risk, reduce it so far as is practicable; and (b) so far as is practicable, contain within the premises the dangerous goods that have been spilled or leaked and any solid or liquid effluent arising from an incident. (2) In the case of dangerous goods contained in a tank, the spill containment for that tank must not be shared with any other dangerous goods or other substances that are not compatible with the dangerous goods in the tank. (3) In the event of a spill or leak of dangerous goods, the occupier must ensure that- (a) immediate action is taken to reduce any risk associated with the spill or leak so far as is practicable; and (b) the dangerous goods and any resulting effluent are, as soon as reasonably possible, cleaned up and disposed of or otherwise made safe.
Note on H54: 427. Manifest to be maintained (1) Premises where dangerous goods are stored and handled in quantities that exceed the relevant quantities specified in the column headed "Manifest Quantity" in the table in Schedule 2 are prescribed premises for the purposes of section 30 of the Act. (2) A manifest is in the prescribed form for the purposes of section 30 of the Act if it contains the information specified in Schedule 3. (3) An occupier of prescribed premises must ensure that the manifest is kept on the premises in a place where it is readily accessible to the emergency services authority.
Note on H55: 424. Ignition sources in hazardous areas An occupier of premises where dangerous goods are stored and handled must ensure that, so far as is practicable, ignition sources are not present in any hazardous area within the premises.
Note on H56: 435. Fire protection-general (1) An occupier of premises where dangerous goods are stored and handled must ensure that- (a) the premises are provided with a fire protection system that- (i) is designed and constructed for the types and quantities of dangerous goods and the conditions under which they are stored and handled; and (ii) uses fire fighting media that are compatible with the dangerous goods and are effective in the control of incidents involving the types and quantities of dangerous goods; and (b) the fire protection system is- (i) properly installed, tested and maintained; and (ii) at all times accessible to persons on the premises and to the emergency services authority; and (iii) is capable of being used, without adaptation or modification, with the equipment used by the emergency services authority. (2) The occupier must, if any of the components of the fire protection system are rendered inoperative, ensure that- (a) the implications of any of the components of the system being unserviceable or inoperative are assessed; and (b) alternative measures are taken to control, to the same level of effectiveness, those risks that were controlled by the system when functioning fully; and (c) the fire protection system is returned to full operation as soon as possible. (3) If the implications of the system becoming unserviceable or inoperative, as assessed by the occupier under sub-regulation (2)(a), include a significant reduction in the effectiveness of the fire protection system, the occupier must notify the emergency services authority of the condition of the fire protection system. (4) In determining the alternative measures required under sub-regulation (2)(b) the occupier must have regard to the need for- (a) the provision of alternative fire protection measures; and (b) a reduction of the quantities of dangerous goods; and (c) stopping or limiting the processes used for the storage and handling of dangerous goods; and (d) modifications to systems of work.
Note on H57: 435. Fire protection-general (1) An occupier of premises where dangerous goods are stored and handled must ensure that- (a) the premises are provided with a fire protection system that- (i) is designed and constructed for the types and quantities of dangerous goods and the conditions under which they are stored and handled; and (ii) uses fire fighting media that are compatible with the dangerous goods and are effective in the control of incidents involving the types and quantities of dangerous goods; and (b) the fire protection system is- (i) properly installed, tested and maintained; and (ii) at all times accessible to persons on the premises and to the emergency services authority; and (iii) is capable of being used, without adaptation or modification, with the equipment used by the emergency services authority. (2) The occupier must, if any of the components of the fire protection system are rendered inoperative, ensure that- (a) the implications of any of the components of the system being unserviceable or inoperative are assessed; and (b) alternative measures are taken to control, to the same level of effectiveness, those risks that were controlled by the system when functioning fully; and (c) the fire protection system is returned to full operation as soon as possible. (3) If the implications of the system becoming unserviceable or inoperative, as assessed by the occupier under sub-regulation (2)(a), include a significant reduction in the effectiveness of the fire protection system, the occupier must notify the emergency services authority of the condition of the fire protection system. (4) In determining the alternative measures required under sub-regulation (2)(b) the occupier must have regard to the need for- (a) the provision of alternative fire protection measures; and (b) a reduction of the quantities of dangerous goods; and (c) stopping or limiting the processes used for the storage and handling of dangerous goods; and (d) modifications to systems of work.
Note on H58: 442. Register of dangerous goods (1) An occupier of premises where dangerous goods are stored and handled must ensure that- (a) a register is kept and maintained for the dangerous goods stored and handled; and (b) the register contains a list of all dangerous goods stored and handled at the premises and, if required, a MSDS for each of the dangerous goods; and (c) the register is readily accessible to any person engaged by the occupier to work at the premises and any other person who is likely to be affected by the dangerous goods on the premises. (2) Sub-regulation (1) does not apply to dangerous goods received in packages of such a size that they do not have to be marked under the ADG Code. (3) Sub-regulation (1) does not apply to dangerous goods in transit.
Note on H59: 444. Response to emergencies (1) An occupier of premises where dangerous goods are stored and handled must respond to an emergency at the premises by ensuring that- (a) immediate action is taken to assess and control any risk associated with the emergency, including making any plant or equipment associated with the emergency and the surrounding area safe so far as is practicable; and (b) only persons essential to carrying out the action referred to in paragraph (a) remain in the vicinity of the emergency; and (c) the risk to each person engaged by the occupier at the premises to carry out the action referred to in paragraph (a) is reduced so far as is practicable. (2) The duties of the occupier under sub-regulations (1)(b) and (1)(c) do not extend to members of the emergency services authority responding to the emergency.
Note on H60: 445. Investigation of incidents (1) An occupier of premises where dangerous goods are stored and handled must ensure that- (a) any incident occurring at the premises is investigated and that the investigation, so far as possible, determines the cause or likely cause of the incident; and (b) a record of the investigation of the incident is- (i) made; and (ii) kept for at least 5 years; and (iii) readily available, on request, to the Authority.
Note on H61: 446. Risk assessment and control following incidents The occupier of premises where an incident has occurred must- (a) review the risk assessment carried out in accordance with regulation 405, taking into account the results of the investigation into the incident; and (b) if the review identifies deficiencies in any risk control measures, alter those measures or implement new measures in accordance with this Part.
Note on H62: 506. Notification to Authority (1) An occupier of premises where dangerous goods are stored and handled in quantities that exceed the relevant quantities specified in the column headed "Manifest Quantity" in the table in Schedule 2, must ensure that the Authority is notified of the presence of those dangerous goods. (2) A notification to the Authority under sub-regulation (1) must- (a) be given within 14 days after the obligation to notify arises; and (b) include the following information- (i) the name of the occupier; and (ii) the address of the premises where the dangerous goods are stored and handled; and (iii) the occupier's contact details; and (iv) the nature of the principal activities involving the dangerous goods; and (v) the Class and the maximum quantity of the dangerous goods stored and handled in bulk or as packaged dangerous goods; and (vi) descriptions and details and the maximum quantity of any C1 combustible liquids stored and handled in bulk or as packaged dangerous goods; and (vii) the product name and the maximum quantity of goods too dangerous to be transported. (3) The occupier must ensure that the Authority is provided with further notification, containing the information required under sub-regulation (2), every 2 years, or at such longer intervals as are specified by the Authority.
Note on H63: 405. Risk assessment (1) If a hazard is identified under regulation 404, an occupier of premises where dangerous goods are stored and handled must ensure that an assessment is made of the risks associated with the hazard. (2) Without limiting the generality of sub-regulation (1), the occupier, in conducting an assessment of risk, must have regard to the matters specified in regulation 404(2) so far as they relate to the storage and handling of dangerous goods at the premises. (3) The occupier must review the assessment- (a) if there is a significant change to any process or system of work in relation to the storage and handling of dangerous goods; and (b) if there is evidence to indicate that the risk assessment no longer adequately assesses the risk associated with any hazard; and (c) if required to do so under regulation 446 as a result of an incident occurring at the premises; and (d) at intervals of not more than 5 years from the assessment or last review. (4) The occupier must- (a) make a record of the assessment and any review of the assessment; and (b) keep a copy of that record while the assessment is current or being reviewed.
Note on H66: 3.3 ELECTRICAL INSTALLATIONS AND EQUIPMENT The following requirements shall apply to both electrical equipment and installations in areas designated as hazardous areas under AS/NZS 2430: (a) Electrical installations All electrical installations shall be installed in compliance with the provisions of AS/NZS 3000 that relate to electrical equipment in hazardous locations. The equipment shall be of a type certified to comply with the relevant Australian Standard or that has been approved for use in such locations by the relevant authority. (b) Portable and mobile electrical equipment All electrical equipment to which AS/NZS 3000 does not apply shall be of a type certified to comply with the relevant Australian Standard or that has been approved for use in such locations by the relevant authority, except where Item (c) below applies. (c) Electric forklift trucks In hazardous areas classified as Zone 2, electric forklift trucks and similar vehicles (e.g. stackers) not suitable for use in the Zone shall not be used except where Appendix D is complied with in all respects. NOTE: Requirements for electric forklift trucks for use in hazardous zones are specified in AS 1915.
Note on H67: 7.2.5 Signs A prominent sign on or near the dispenser shall be marked in letters at least 50 mm high as follows: STOP ENGINE—NO SMOKING The international symbol for ‘smoking prohibited’ may be used in lieu of the words ‘no smoking’. The words ‘no flames, pilot lights or mobile phones’ may also be added. 3.8.2 Signs and notices At the entrance to any storage area greater than minor storage, the following signs shall be displayed: (a) A DANGER—NO SMOKING, NO NAKED FLAMES sign; (b) For flammable liquids, a Class label and Subsidiary risk label (if any). (c) For combustible liquids, a COMBUSTIBLE LIQUID sign. The following signs should be placed at the entrance(s) to the premises: (i) A WARNING—RESTRICTED AREA, AUTHORIZED PERSONNEL ONLY sign. (ii) A sign listing the emergency contact names, titles and phone numbers relevant to the installation. (iii) The name, address and phone number of the occupier. (iv) A layout diagram showing the location of fixed fire protection facilities (where installed), the drainage system and the ‘Emergency Stop’ switch. Where two or more points of access are adjacent to each other so that a single set of signs and notices are clearly readable from each point of access, duplicate signs and notices are not required. Signs shall comply with AS 1319. Class labels shall conform to AS 1216 and be a minimum of 250 mm square. Other signs shall have lettering at least 50 mm high. NOTE: Composite signs or pictographs complying with the above requirements may be used.
Note on H69: 7.3.5 Unsupervised self-service systems Any dispenser that is operated by a customer by means of currency or other means of payment, e.g. credit card, shall comply with the requirements of this Clause (7.3.5) as appropriate, and the following: (a) The dispenser hose shall be shorter than the distance from the dispenser to the nearest building or to the nearest boundary of an adjacent property. (b) The area around the dispenser and the payment unit shall be lit in accordance with Clause 3.5 at all times during which the unit is available for service. (c) The installation shall include an emergency shut-down device having the following functions or features: (i) When activated, the emergency device shall shut off the dispenser pump and transmit an alarm to a person or organization capable of responding. NOTE: It may also be used to release the access to the fire extinguishers (see Clause 11.9). (ii) It shall be readily accessible, and shall be integral with or adjacent to the currency or card receptor. (iii) It shall be protected from vandalism or unwarranted operation by a break-glass screen or equivalent. (iv) A notice shall be displayed, giving instructions on how to operate the device in the event of a major spill or fire.
Note on H70: 7.2.4 Emergency power cut-off A clearly identified switch or circuit-breaker which will enable the power to be shut off to all dispensing units shall be provided at a location remote from any dispensing unit and easily accessible in an emergency. NOTE: Consideration should be given to incorporating a single emergency stop that would shut off all fuel dispensing.
Note on H71: 7.4.2 Customer-operated nozzles The delivery nozzle for flammable liquids dispenser that is intended to be operated by a customer shall not have a latching device. No item, e.g. fuel cap, keys or any other device, shall be used to hold open a customer-operated nozzle.
Note on H72: 11.7 FIRE PROTECTION REQUIREMENTS FOR TANK VEHICLE TRANSFER AREAS 11.7.1 Location of extinguishers The positions of extinguishers shall be chosen to optimize access in an emergency. The following considerations should be taken into account: (a) At least one powder-type extinguisher should be at ground level at each loading position. For a top-loading installation at least one additional powder-type extinguisher should be at the loading platform. (b) All foam type extinguishers should be at ground level within 10 m of the loading point. (c) Locations should be on approach or exit paths. (d) Access to any extinguisher should not be vulnerable to blockage by a fire.
Note on H73: 8.2.4 Collision protection A tank vehicle filling facility shall be protected against damage from vehicles and forklift trucks by a guard rail, traffic bollards or other physical barriers.
Note on H74: 7.2 GENERAL REQUIREMENTS 7.2.1 Storage method Any flammable or combustible liquid in quantities exceeding those dealt with in Section 2 shall be kept in package stores or tanks in accordance with Sections 3, 4 and 5 as appropriate. 7.2.2 High-level tanks Any tank which is so situated as to produce a gravity head at the dispenser shall be equipped with a fail-safe solenoid valve or other equally effective device which shuts off the supply at the tank outlet except when the dispenser is in use. Where the tank is either Category 1 or 2 and there is no metering dispenser, a manual shut-off valve shall be provided at the tank. 7.2.3 Gaseous fuels Where gaseous fuels for vehicles are stored, handled and dispensed on the premises, the following provisions shall be observed: (a) AS/NZS 1596 for LP Gas. (b) AS 3961 for LNG. (c) AG 901 for CNG. 7.2.4 Emergency power cut-off A clearly identified switch or circuit-breaker which will enable the power to be shut off to all dispensing units shall be provided at a location remote from any dispensing unit and easily accessible in an emergency. NOTE: Consideration should be given to incorporating a single emergency stop that would shut off all fuel dispensing. 7.2.5 Signs A prominent sign on or near the dispenser shall be marked in letters at least 50 mm high as follows: STOP ENGINE—NO SMOKING The international symbol for ‘smoking prohibited’ may be used in lieu of the words ‘no smoking’. The words ‘no flames, pilot lights or mobile phones’ may also be added. 7.2.6 Hazardous zones The hazardous zones for dispensers as defined in the AS/NZS 2430.3 series differentiate between petrol and LP Gas so care should be taken to consider the interrelation of the two zones where both fuels are being dispensed.
Note on H75: 7.6.2 Procedures Operating procedures shall take into account the following: (a) The prevention of smoking or any other ignition sources within 3 m of any point where flammable liquid might be exposed, particularly when receiving or dispensing. (b) The need to switch off a vehicle’s engine while refuelling. (c) Any possibility that vapour from a flammable liquid fill or vent pipe could reach an internal pilot flame on a campervan or caravan if the appliance vent has been badly located in relation to the filler (in such cases it is necessary to turn off the pilot before filling). (d) The prevention of overfilling and spillage when storage tanks are being replenished. (e) The maintenance of fill and dip caps in a liquid-tight condition. (f) The suitability of containers being filled at dispensers for use, i.e. container condition and material, the presence of an effective cap, correct labelling. Containers shall not be filled when inside a vehicle compartment (see also Clause 7.6.3). g) Specific instructions that do not allow the filling of plastic containers that do not comply with AS/NZS 2906 or equivalent Standard. (h) Risks when cleaning parts with flammable liquid. (i) Procedures to be followed in the event of spillage, and particularly the spillage of flammable liquid on clothing. (j) Risks when draining fuel tanks, particularly over inspection pits. (k) Precautions for hot work on vehicle fuel tanks. (l) Safety of electrical equipment used in pits. (m) Floors shall not be washed with flammable liquid. (n) Emergency clean-up equipment shall be available in case of spillage. (o) Persons under the age of 15 years shall be prevented from operating fuel dispensers. (p) Precautions for working in confined spaces. (q) Training in the use of emergency equipment and maintenance of appropriate records. 7.6.3 Filling of containers at dispensers Flammable liquids shall not be filled from a service station’s fuel dispenser into a container unless— (a) the capacity of the container is not greater than 25 L; and (b) the container complies with AS/NZS 2906 or equivalent Standard, or is substantially leakproof, metal, and has a tight-fitting closure; or (c) the container is an approved portable fuel tank for a boat. Any container shall be on the ground whilst being filled, and not in a car boot or the back of a utility vehicle. NOTE: Approved portable fuel tanks for boats may be filled in situ.
Note on H76: 5.4.4 Vent outlet location The discharge point of a vent shall comply with the following requirements: (a) The vent discharge point shall be located laterally at least 4 m for flammable liquids and 2 m for combustible liquids from any opening into a building, e.g., window, door, ventilator, airconditioner or a mechanical vent intake to reduce the possibility of the entry of nuisance vapour. The vent shall be located such that the opening into a building shall be outside the hazardous zone specified in the relevant part of AS/NZS 2430.3. NOTE: The vent for any above-ground tank may discharge at a point at least 150 mm above the top of the tank, provided that other requirements for tank and vent locations are met. (b) The vent discharge point shall be located at least 4 m above ground level except for direct-vented tanks of Categories 1 or 2. (c) Where the tank is to be filled by gravity flow from a tank vehicle, the vent discharge point for the tank shall be at least 4 m above ground level at the fill point and in all circumstances shall be higher than the tank vehicle. (d) Where a Category 1 to 5 tank is to be filled by pumping from a tank vehicle— (i) the vent pipe or overfill point shall terminate in view of the filling operator; or (ii) the tank shall be fitted with a high level alarm audible to the filling operator. Notwithstanding other requirements in this Clause, a vent provision may be connected to a vapour recovery or collection system. NOTE: When filling rates are high, the velocity of the discharging vapour may be high enough to carry it a considerable distance. In such cases, particular attention should be paid to direction of discharge, to vapour diffusion and to potential ignition sources, especially for flammable liquid.
Note on H77: 5.4.5 Vent terminals The discharge end of a vent shall be protected from the ingress of foreign material by means of a protective cage or fitting. Where a tank contains flammable liquid and the vapour within the ullage space of the tank is within explosive limits, a flame arrester or similar device shall be fitted. Any such protective cage, flame arrester or other means shall not reduce the required effective vent area or create undue back-pressure within the tank. NOTE: A flame arrester incorporating a bronze or stainless steel wire mesh having openings not greater than 600 μm is acceptable.
Note on H80: APPENDIX L DECANTING PROCEDURE (Informative) The following procedure should be followed when filling cylinders by decanting: (a) Inspect the customer’s cylinder for corrosion and dents, paying particular attention to the underside of the cylinder. If significant corrosion is present, do not fill the cylinder and refer the customer to a registered cylinder test station. (b) Unlock the decant vessel cover/valve. Ensure that the dead-man’s valve on the filling assembly is closed and the assembly is tightly connected to the storage vessel. Gloves should be worn when decanting. (c) Connect filling assembly (hose) to customer’s cylinder. (d) Open the main valve on customer’s cylinder. (e) Check that the bleed valve on the customer’s cylinder is directed away from the operator and towards a well-ventilated area before opening the bleed valve one half turn using the correct tool. This will reduce the pressure in the customer’s cylinder to be filled. (f) Open the main valve on the decant vessel. (g) Activate the dead-man’s valve on the filling assembly to start the filling process.(h) Stay in attendance during the entire process of filling. Do not use any device (i.e. clamps, rubber bands) to hold the dead-man’s valve open. Observe the hose and all connections during filling for possible leaks. (i) Allow the filling to continue until white cloud/mist emerges from the customer’s cylinder bleed valve, which indicates that the cylinder is full (the maximum fill level has been reached). (j) Immediately release the dead-man’s valve to stop filling. (k) Remove a glove and touch the main decant vessel with bare hands (to discharge any static electricity from the body of the person decanting). Replace the glove and continue. (l) Close the main valve on the customer’s cylinder. (m) After white cloud/mist disappears, close the bleed valve on the customer’s cylinder. Do not close the bleed valve while white cloud/mist is still emerging. (n) Close the main valve on the decant vessel. (o) Carefully disconnect the filling assembly hose from the customer’s cylinder. When breaking the connection, a small amount of vapour trapped between the two valves will escape. (p) Confirm the customer’s cylinder is leak free by applying soapy water with a small paint brush or spray bottle to the following: (i) Outlet of the main valve. (ii) Thread where the main valve is attached to the customer’s cylinder. (iii) Bleed valve opening. (q) Lock the cover/valve of the decant vessel. (r) If LP Gas in liquid form comes in contact with the bare skin or eyes, wash the affected areas with water for at least 10 min and see a doctor. NOTE: Figure L1 provides clarification of decanting equipment terminology.
Note on H81: 7.4.3 Location A decanting cylinder shall not be stored indoors, used indoors or used in a portable application and shall be located on the ground in a static position. Whether decanting froma tank or a cylinder, the design of the installation shall be such that the point of connection to the cylinder being filled cannot lie within the following separation distance: (a) To an opening into a building ....................................................................... 2 m. (b) To buildings on neighbouring property or to any combustible materials stored above ground .......................................................... 5 m. (c) To public places ....................................................................................... 3 m. (d) To any above-ground tank containing dangerous goods ....................................... 3 m. (e) To dispensers for any type of fuel................................................................. 3 m. (f) To the entrance to a drain, pit, or basement ..................................................... 3 m. (g) To any structure limiting egress past the point of connection to the cylinder ........................................................................... 2 m. NOTES: 1 The point of connection implies hose reach if flexible decanting hoses are used. Except where LP Gas decanting is carried out on a dedicated area clearly marked on the ground or on a cylinder stand, the separation distances may be taken from the marked area or stand. 2 The above requirements are displayed in Figure 7.1.
Note on H82: 7.4.3 Location A decanting cylinder shall not be stored indoors, used indoors or used in a portable application and shall be located on the ground in a static position. Whether decanting froma tank or a cylinder, the design of the installation shall be such that the point of connection to the cylinder being filled cannot lie within the following separation distance: (a) To an opening into a building ....................................................................... 2 m. (b) To buildings on neighbouring property or to any combustible materials stored above ground .......................................................... 5 m. (c) To public places ....................................................................................... 3 m. (d) To any above-ground tank containing dangerous goods ....................................... 3 m. (e) To dispensers for any type of fuel................................................................. 3 m. (f) To the entrance to a drain, pit, or basement ..................................................... 3 m. (g) To any structure limiting egress past the point of connection to the cylinder ........................................................................... 2 m. NOTES: 1 The point of connection implies hose reach if flexible decanting hoses are used. Except where LP Gas decanting is carried out on a dedicated area clearly marked on the ground or on a cylinder stand, the separation distances may be taken from the marked area or stand. 2 The above requirements are displayed in Figure 7.1.
Note on H83: 7.4.3 Location A decanting cylinder shall not be stored indoors, used indoors or used in a portable application and shall be located on the ground in a static position. Whether decanting froma tank or a cylinder, the design of the installation shall be such that the point of connection to the cylinder being filled cannot lie within the following separation distance: (a) To an opening into a building ....................................................................... 2 m. (b) To buildings on neighbouring property or to any combustible materials stored above ground .......................................................... 5 m. (c) To public places ....................................................................................... 3 m. (d) To any above-ground tank containing dangerous goods ....................................... 3 m. (e) To dispensers for any type of fuel................................................................. 3 m. (f) To the entrance to a drain, pit, or basement ..................................................... 3 m. (g) To any structure limiting egress past the point of connection to the cylinder ........................................................................... 2 m. NOTES: 1 The point of connection implies hose reach if flexible decanting hoses are used. Except where LP Gas decanting is carried out on a dedicated area clearly marked on the ground or on a cylinder stand, the separation distances may be taken from the marked area or stand. 2 The above requirements are displayed in Figure 7.1.
Note on H84: 7.4.3 Location A decanting cylinder shall not be stored indoors, used indoors or used in a portable application and shall be located on the ground in a static position. Whether decanting froma tank or a cylinder, the design of the installation shall be such that the point of connection to the cylinder being filled cannot lie within the following separation distance: (a) To an opening into a building ....................................................................... 2 m. (b) To buildings on neighbouring property or to any combustible materials stored above ground .......................................................... 5 m. (c) To public places ....................................................................................... 3 m. (d) To any above-ground tank containing dangerous goods ....................................... 3 m. (e) To dispensers for any type of fuel................................................................. 3 m. (f) To the entrance to a drain, pit, or basement ..................................................... 3 m. (g) To any structure limiting egress past the point of connection to the cylinder ........................................................................... 2 m. NOTES: 1 The point of connection implies hose reach if flexible decanting hoses are used. Except where LP Gas decanting is carried out on a dedicated area clearly marked on the ground or on a cylinder stand, the separation distances may be taken from the marked area or stand. 2 The above requirements are displayed in Figure 7.1.
Note on H85: 7.4.3 Location A decanting cylinder shall not be stored indoors, used indoors or used in a portable application and shall be located on the ground in a static position. Whether decanting froma tank or a cylinder, the design of the installation shall be such that the point of connection to the cylinder being filled cannot lie within the following separation distance: (a) To an opening into a building ....................................................................... 2 m. (b) To buildings on neighbouring property or to any combustible materials stored above ground .......................................................... 5 m. (c) To public places ....................................................................................... 3 m. (d) To any above-ground tank containing dangerous goods ....................................... 3 m. (e) To dispensers for any type of fuel................................................................. 3 m. (f) To the entrance to a drain, pit, or basement ..................................................... 3 m. (g) To any structure limiting egress past the point of connection to the cylinder ........................................................................... 2 m. NOTES: 1 The point of connection implies hose reach if flexible decanting hoses are used. Except where LP Gas decanting is carried out on a dedicated area clearly marked on the ground or on a cylinder stand, the separation distances may be taken from the marked area or stand. 2 The above requirements are displayed in Figure 7.1.
Note on H86: 7.4.3 Location A decanting cylinder shall not be stored indoors, used indoors or used in a portable application and shall be located on the ground in a static position. Whether decanting froma tank or a cylinder, the design of the installation shall be such that the point of connection to the cylinder being filled cannot lie within the following separation distance: (a) To an opening into a building ....................................................................... 2 m. (b) To buildings on neighbouring property or to any combustible materials stored above ground .......................................................... 5 m. (c) To public places ....................................................................................... 3 m. (d) To any above-ground tank containing dangerous goods ....................................... 3 m. (e) To dispensers for any type of fuel................................................................. 3 m. (f) To the entrance to a drain, pit, or basement ..................................................... 3 m. (g) To any structure limiting egress past the point of connection to the cylinder ........................................................................... 2 m. NOTES: 1 The point of connection implies hose reach if flexible decanting hoses are used. Except where LP Gas decanting is carried out on a dedicated area clearly marked on the ground or on a cylinder stand, the separation distances may be taken from the marked area or stand. 2 The above requirements are displayed in Figure 7.1.
Note on H87: 7.4.3 Location A decanting cylinder shall not be stored indoors, used indoors or used in a portable application and shall be located on the ground in a static position. Whether decanting froma tank or a cylinder, the design of the installation shall be such that the point of connection to the cylinder being filled cannot lie within the following separation distance: (a) To an opening into a building ....................................................................... 2 m. (b) To buildings on neighbouring property or to any combustible materials stored above ground .......................................................... 5 m. (c) To public places ....................................................................................... 3 m. (d) To any above-ground tank containing dangerous goods ....................................... 3 m. (e) To dispensers for any type of fuel................................................................. 3 m. (f) To the entrance to a drain, pit, or basement ..................................................... 3 m. (g) To any structure limiting egress past the point of connection to the cylinder ........................................................................... 2 m. NOTES: 1 The point of connection implies hose reach if flexible decanting hoses are used. Except where LP Gas decanting is carried out on a dedicated area clearly marked on the ground or on a cylinder stand, the separation distances may be taken from the marked area or stand. 2 The above requirements are displayed in Figure 7.1.
Note on H88: 9.5.19 Decanting cylinders Any LP Gas cylinder provided for the filling of other LP Gas cylinders by decanting shall be located not less than 5 m from any above-ground LP Gas storage tank, unless the tank is protected from a fire at the decanting cylinder. A firewall constructed in accordance with Clause 4.4 is deemed to provide suitable protection. The outlet and safety relief valves of the decant cylinder shall be directed away from the storage tank. Apart from the provisions of this Clause (Clause 9.5.19), all provisions of the relevant Sections of this Standard shall apply to the operation of decanting cylinders.
Note on H89: 3.4.1 Provision of safety valves Safety valves shall be provided as required by the pressure vessel design code, with the following qualifications: (a) A safety valve shall communicate with the vapour space in the tank. (b) Safety valves shall be arranged so that the possibility of tampering is minimized. Any externally located pressure-setting adjustment shall be provided with a means of sealing or locking after setting. (c) Safety valves shall comply with AS 1271 or UL132 or other recognized Standard. NOTE: Care is necessary in determining the setting and capacity of safety valves for tanks with provisions for controlling the service temperature (see Clause 3.2.1(b)(iii)) if the temperature of the LP Gas delivered is likely to be higher than the controlled design temperature). (d) In Australia only, the aggregate discharge capacity of the safety valve(s) shall be not less than that determined in accordance with Appendix E. NOTE: Appendix E has been derived from the general formula of AS 1210, simplified to suit the particular case of LP Gas. 3.4.2 Discharge provisions A safety valve and any discharge piping shall comply with the following requirements when installed: (a) The size of any discharge piping shall be sufficient to ensure that the required discharge capacity of a safety valve is achieved. The effect of back pressure shall be taken into account in the case of changes of direction or excessive length. (b) The direction of discharge shall be vertically upwards. (c) Except for measures necessary to prevent ingress of rainwater or blockage, venting shall be direct to atmosphere. (d) The direction of discharge shall not permit escaping vapour to impinge on any tank, fitting, structure or piping. (e) It shall not be possible to render a safety valve inoperative except under the conditions permitted in Clause 3.4.3. (f) The discharge for a tank of more than 8 kL capacity shall terminate not less than 2 m above the tank. (g) Where a lockable dome or cage is provided, the arrangement shall continue to comply with the requirements relating to free dispersal or impingement of discharge. (h) The outlet shall be protected as far as practicable from physical damage. (i) A cap shall be provided to prevent the accumulation of rain, dew or foreign matter within the safety valve in such a manner as to render the valve defective. Where a discharge pipe is fitted, the cap shall be fitted at the point of discharge. The cap shall not prevent the safety valve from operating effectively and shall not prevent the effective discharge, in a safe manner, of any release of LP Gas. Where a weep hole or drain is provided in order to comply with this requirement, the overall design shall be such that any ignited LP Gas discharge cannot impinge on the tank, adjacent tanks, piping, or equipment. NOTE: A deflector or a drainage discharge pipe is permissible, provided that piping does not incorporate a valve. (j) A means shall be provided to protect the safety relief valve from impact or high wind loading on the discharge piping which could damage the valve. 3.4.3 Reserve safety valves Where additional safety valves are provided to permit servicing without depressurizing, the valve system used to isolate any individual safety valve shall be designed so that it is not at any time possible to operate the system with less aggregate pressure-relief capacity than that required under Clause 3.4.1(c).
Note on H90: 3.4.1 Provision of safety valves Safety valves shall be provided as required by the pressure vessel design code, with the following qualifications: (a) A safety valve shall communicate with the vapour space in the tank. (b) Safety valves shall be arranged so that the possibility of tampering is minimized. Any externally located pressure-setting adjustment shall be provided with a means of sealing or locking after setting. (c) Safety valves shall comply with AS 1271 or UL132 or other recognized Standard. NOTE: Care is necessary in determining the setting and capacity of safety valves for tanks with provisions for controlling the service temperature (see Clause 3.2.1(b)(iii)) if the temperature of the LP Gas delivered is likely to be higher than the controlled design temperature). (d) In Australia only, the aggregate discharge capacity of the safety valve(s) shall be not less than that determined in accordance with Appendix E. NOTE: Appendix E has been derived from the general formula of AS 1210, simplified to suit the particular case of LP Gas. 3.4.2 Discharge provisions A safety valve and any discharge piping shall comply with the following requirements when installed: (a) The size of any discharge piping shall be sufficient to ensure that the required discharge capacity of a safety valve is achieved. The effect of back pressure shall be taken into account in the case of changes of direction or excessive length. (b) The direction of discharge shall be vertically upwards. (c) Except for measures necessary to prevent ingress of rainwater or blockage, venting shall be direct to atmosphere. (d) The direction of discharge shall not permit escaping vapour to impinge on any tank, fitting, structure or piping. (e) It shall not be possible to render a safety valve inoperative except under the conditions permitted in Clause 3.4.3. (f) The discharge for a tank of more than 8 kL capacity shall terminate not less than 2 m above the tank. (g) Where a lockable dome or cage is provided, the arrangement shall continue to comply with the requirements relating to free dispersal or impingement of discharge. (h) The outlet shall be protected as far as practicable from physical damage. (i) A cap shall be provided to prevent the accumulation of rain, dew or foreign matter within the safety valve in such a manner as to render the valve defective. Where a discharge pipe is fitted, the cap shall be fitted at the point of discharge. The cap shall not prevent the safety valve from operating effectively and shall not prevent the effective discharge, in a safe manner, of any release of LP Gas. Where a weep hole or drain is provided in order to comply with this requirement, the overall design shall be such that any ignited LP Gas discharge cannot impinge on the tank, adjacent tanks, piping, or equipment. NOTE: A deflector or a drainage discharge pipe is permissible, provided that piping does not incorporate a valve. (j) A means shall be provided to protect the safety relief valve from impact or high wind loading on the discharge piping which could damage the valve. 3.4.3 Reserve safety valves Where additional safety valves are provided to permit servicing without depressurizing, the valve system used to isolate any individual safety valve shall be designed so that it is not at any time possible to operate the system with less aggregate pressure-relief capacity than that required under Clause 3.4.1(c).
Note on H91: 3.3.4 Primary shut-down system The primary shut-down provision shall consist of a non-return valve, except that where outward flow is necessary an excess-flow valve may be used. The design and installation of the valve shall be such that it will continue to function as a shut-down device should impact or shear-off occur to any external portion or attachment. Where a multiple function valve which complies with Clause 3.3.1(e) is used, a primary shut-down system is not required.
Note on H92: 3.3.5 Secondary shut-down system Where the primary shut-down provision is a non-return valve, the secondary system shall comprise at least a manual positive shut-off valve, or, if the tank is 8 kL or less and the entry is for filling into the vapour space, another non-return valve that is gastight. Where the primary shut-down provision is an excess-flow valve, the secondary system shall comprise— (a) for vapour connections . . . at least a manual positive shut-off valve; or (b) for liquid connections . . . an emergency shut-down system, except that for an opening into a tank that is not larger than 3/4 NPT and that is used only for decanting into cylinders, a manual positive shut-off valve is permissible. NOTE: Clauses 3.3.4 and 3.3.5 should be read as specifying functions and not necessarily selfcontained and independent valves. The primary and the secondary functions may be incorporated in a single compound valve provided that all the functional requirements are incorporated.
Note on H93: 3.5.4 Liquid level and contents A tank shall be fitted with the following: (a) A separate fixed liquid level gauge arranged to indicate the standard filling level, which shall be determined in accordance with Appendix C. (b) A means for monitoring the whole range of the liquid contents of the tank. NOTE: A tank may be fitted with the following: (c) Additional fixed liquid level gauges located to indicate the standard filling level for different LP Gas compositions. (d) A variable liquid level gauge to permit the use of the temperature-correction method of filling to the maximum filling level. (e) A contents gauge to indicate the liquid contents or surface level as it varies with consumption and replenishment.
Note on H94: 3.5.5 Pressure gauges Each tank shall be fitted with a pressure gauge complying with AS 1349/NZS/AS 1349.
Note on H95: 3.5.8 Provision for emptying tank Every tank shall have a means for removing liquid LP Gas from the tank should an emergency arise. Where the piping system cannot perform this function, an additional provision shall be made in the form of a drain or an eductor tube, fitted with an excess flow and shut-off valve. The shut-off valve outlet shall be capped or plugged, when not in use, with a metal fitting, and Table 3.2 shall apply. The outlet shall be directed so as to avoid impingement on the tank and fittings, supports, or other tanks. NOTES: 1 Because bottom drain fittings on small tanks may be difficult to access and vulnerable to damage, eductor tubes may be preferable. 2 Devices which are plugged when not in use and incorporate a check valve with an excessflow function that is enabled by the insertion of a screw-in fitting are acceptable as primary and secondary protection for tanks up to 8 kL capacity and may serve as a means of emptying the tank.
Note on H96: 3.5.9 Electrical equipment Electrical equipment and wiring shall comply with AS/NZS 3000/New Zealand Electricity Regulations 1993.
Note on H97: 4.2.1 General location and spacing Above-ground storage tanks shall be located in accordance with the distances shown in Table 4.1, with the following qualifications: (a) An above-ground tank shall not be installed in a building. (b) Where the site is used primarily for LP Gas storage and handling, or where the LP Gas facility is within a petroleum terminal, the separation distance to buildings on the same site as the LP Gas storage may be halved, provided that in no case shall a tank having a total capacity exceeding 2.5 kL be located closer than 3 m to such a building. (c) A tank exceeding 0.5 kL capacity shall be not less than 1 m from a boundary. (d) Where a tank under 0.5 kL capacity is permitted with zero distance to public places or protected places, the space in the opposite direction shall be clear for a minimum distance of 3 m. No more than five such tanks shall be installed in a group with 1.5 m to a public place and zero to a protected place (see Appendix F for an illustration of the application of separation distances).
Note on H100: 4.2.6 On-site storages and flammable and combustible materials LP Gas tanks shall be separated from stores of flammable or combustible materials as follows: (a) At least 6 m from any above-ground tank, package store or filling area for flammable or combustible materials. (b) At least 3 m from the top of the bund of a compound in which flammable liquids are stored. (c) At least 2 m from any vent outlet of flammable liquids store (measured horizontally). (d) For stores of flammable liquids, as determined by AS 1940 or this Standard, whichever is greater.
Note on H106: 9.3.2 Style A dispenser system Where a Style A dispenser system is required by Figure 9.2, it shall include a dispenser which complies with AS 2229.2/NZS 6109.2 and which is provided with an excess-flow valve, a remote-operated shut-off valve, and a pipe-shear provision, in that order, in all LP Gas pipes attached to the cabinet. The valves shall be below or as close as possible to ground level, with the shear provision above them. Where the remote-operated valve can be relied upon to shut off automatically in the event of pipe shear the excess-flow valve may be omitted. (Additional requirements for service station dispensers are provided in Clause 9.5.16). In addition, the system shall incorporate the following: (a) Control valves The following control valves shall be provided inside the dispenser cabinet and as close as practicable to the flexible hose between the dispenser cabinet and the breakaway coupling: (i) A manually operated positive shut-off valve. (ii) An excess-flow valve. (b) Overspeed sensor A device shall be fitted to the dispensing equipment which has the ability to detect an abnormal flow of fuel, e.g. caused by a hose rupture, and which will shut down the dispenser and the remote pump. (c) Pump control A switch shall be fitted inside the dispensing cabinet which can shut down the remote pump. NOTE: This switching action may be performed automatically by the positioning of the hose nozzle in and out of its receptacle. (d) Return line In Australia, a return line from a dispenser shall comply with the requirements of Table 3.2 for liquid withdrawal or two-way flow. In New Zealand, the return line shall comply with the requirements for vapour return and balancing lines. A continuous liquid bypass in the dispenser shall be limited to a flow area of less than 4 mm2. NOTE: Use of bollards or guardrails to protect the dispenser from minor impact is considered good practice but is not mandatory.
Note on H107: 9.3.2 Style A dispenser system Where a Style A dispenser system is required by Figure 9.2, it shall include a dispenser which complies with AS 2229.2/NZS 6109.2 and which is provided with an excess-flow valve, a remote-operated shut-off valve, and a pipe-shear provision, in that order, in all LP Gas pipes attached to the cabinet. The valves shall be below or as close as possible to ground level, with the shear provision above them. Where the remote-operated valve can be relied upon to shut off automatically in the event of pipe shear the excess-flow valve may be omitted. (Additional requirements for service station dispensers are provided in Clause 9.5.16). In addition, the system shall incorporate the following: (a) Control valves The following control valves shall be provided inside the dispenser cabinet and as close as practicable to the flexible hose between the dispenser cabinet and the breakaway coupling: (i) A manually operated positive shut-off valve. (ii) An excess-flow valve. (b) Overspeed sensor A device shall be fitted to the dispensing equipment which has the ability to detect an abnormal flow of fuel, e.g. caused by a hose rupture, and which will shut down the dispenser and the remote pump. (c) Pump control A switch shall be fitted inside the dispensing cabinet which can shut down the remote pump. NOTE: This switching action may be performed automatically by the positioning of the hose nozzle in and out of its receptacle. (d) Return line In Australia, a return line from a dispenser shall comply with the requirements of Table 3.2 for liquid withdrawal or two-way flow. In New Zealand, the return line shall comply with the requirements for vapour return and balancing lines. A continuous liquid bypass in the dispenser shall be limited to a flow area of less than 4 mm2. NOTE: Use of bollards or guardrails to protect the dispenser from minor impact is considered good practice but is not mandatory.
Note on H108: 9.3.2 Style A dispenser system Where a Style A dispenser system is required by Figure 9.2, it shall include a dispenser which complies with AS 2229.2/NZS 6109.2 and which is provided with an excess-flow valve, a remote-operated shut-off valve, and a pipe-shear provision, in that order, in all LP Gas pipes attached to the cabinet. The valves shall be below or as close as possible to ground level, with the shear provision above them. Where the remote-operated valve can be relied upon to shut off automatically in the event of pipe shear the excess-flow valve may be omitted. (Additional requirements for service station dispensers are provided in Clause 9.5.16). In addition, the system shall incorporate the following: (a) Control valves The following control valves shall be provided inside the dispenser cabinet and as close as practicable to the flexible hose between the dispenser cabinet and the breakaway coupling: (i) A manually operated positive shut-off valve. (ii) An excess-flow valve. (b) Overspeed sensor A device shall be fitted to the dispensing equipment which has the ability to detect an abnormal flow of fuel, e.g. caused by a hose rupture, and which will shut down the dispenser and the remote pump. (c) Pump control A switch shall be fitted inside the dispensing cabinet which can shut down the remote pump. NOTE: This switching action may be performed automatically by the positioning of the hose nozzle in and out of its receptacle. (d) Return line In Australia, a return line from a dispenser shall comply with the requirements of Table 3.2 for liquid withdrawal or two-way flow. In New Zealand, the return line shall comply with the requirements for vapour return and balancing lines. A continuous liquid bypass in the dispenser shall be limited to a flow area of less than 4 mm2. NOTE: Use of bollards or guardrails to protect the dispenser from minor impact is considered good practice but is not mandatory.
Note on H109: 9.3.2 Style A dispenser system Where a Style A dispenser system is required by Figure 9.2, it shall include a dispenser which complies with AS 2229.2/NZS 6109.2 and which is provided with an excess-flow valve, a remote-operated shut-off valve, and a pipe-shear provision, in that order, in all LP Gas pipes attached to the cabinet. The valves shall be below or as close as possible to ground level, with the shear provision above them. Where the remote-operated valve can be relied upon to shut off automatically in the event of pipe shear the excess-flow valve may be omitted. (Additional requirements for service station dispensers are provided in Clause 9.5.16). In addition, the system shall incorporate the following: (a) Control valves The following control valves shall be provided inside the dispenser cabinet and as close as practicable to the flexible hose between the dispenser cabinet and the breakaway coupling: (i) A manually operated positive shut-off valve. (ii) An excess-flow valve. (b) Overspeed sensor A device shall be fitted to the dispensing equipment which has the ability to detect an abnormal flow of fuel, e.g. caused by a hose rupture, and which will shut down the dispenser and the remote pump. (c) Pump control A switch shall be fitted inside the dispensing cabinet which can shut down the remote pump. NOTE: This switching action may be performed automatically by the positioning of the hose nozzle in and out of its receptacle. (d) Return line In Australia, a return line from a dispenser shall comply with the requirements of Table 3.2 for liquid withdrawal or two-way flow. In New Zealand, the return line shall comply with the requirements for vapour return and balancing lines. A continuous liquid bypass in the dispenser shall be limited to a flow area of less than 4 mm2. NOTE: Use of bollards or guardrails to protect the dispenser from minor impact is considered good practice but is not mandatory.
Note on H110: 9.3.2 Style A dispenser system Where a Style A dispenser system is required by Figure 9.2, it shall include a dispenser which complies with AS 2229.2/NZS 6109.2 and which is provided with an excess-flow valve, a remote-operated shut-off valve, and a pipe-shear provision, in that order, in all LP Gas pipes attached to the cabinet. The valves shall be below or as close as possible to ground level, with the shear provision above them. Where the remote-operated valve can be relied upon to shut off automatically in the event of pipe shear the excess-flow valve may be omitted. (Additional requirements for service station dispensers are provided in Clause 9.5.16). In addition, the system shall incorporate the following: (a) Control valves The following control valves shall be provided inside the dispenser cabinet and as close as practicable to the flexible hose between the dispenser cabinet and the breakaway coupling: (i) A manually operated positive shut-off valve. (ii) An excess-flow valve. (b) Overspeed sensor A device shall be fitted to the dispensing equipment which has the ability to detect an abnormal flow of fuel, e.g. caused by a hose rupture, and which will shut down the dispenser and the remote pump. (c) Pump control A switch shall be fitted inside the dispensing cabinet which can shut down the remote pump. NOTE: This switching action may be performed automatically by the positioning of the hose nozzle in and out of its receptacle. (d) Return line In Australia, a return line from a dispenser shall comply with the requirements of Table 3.2 for liquid withdrawal or two-way flow. In New Zealand, the return line shall comply with the requirements for vapour return and balancing lines. A continuous liquid bypass in the dispenser shall be limited to a flow area of less than 4 mm2. NOTE: Use of bollards or guardrails to protect the dispenser from minor impact is considered good practice but is not mandatory.
Note on H111: 9.3.2 Style A dispenser system Where a Style A dispenser system is required by Figure 9.2, it shall include a dispenser which complies with AS 2229.2/NZS 6109.2 and which is provided with an excess-flow valve, a remote-operated shut-off valve, and a pipe-shear provision, in that order, in all LP Gas pipes attached to the cabinet. The valves shall be below or as close as possible to ground level, with the shear provision above them. Where the remote-operated valve can be relied upon to shut off automatically in the event of pipe shear the excess-flow valve may be omitted. (Additional requirements for service station dispensers are provided in Clause 9.5.16). In addition, the system shall incorporate the following: (a) Control valves The following control valves shall be provided inside the dispenser cabinet and as close as practicable to the flexible hose between the dispenser cabinet and the breakaway coupling: (i) A manually operated positive shut-off valve. (ii) An excess-flow valve. (b) Overspeed sensor A device shall be fitted to the dispensing equipment which has the ability to detect an abnormal flow of fuel, e.g. caused by a hose rupture, and which will shut down the dispenser and the remote pump. (c) Pump control A switch shall be fitted inside the dispensing cabinet which can shut down the remote pump. NOTE: This switching action may be performed automatically by the positioning of the hose nozzle in and out of its receptacle. (d) Return line In Australia, a return line from a dispenser shall comply with the requirements of Table 3.2 for liquid withdrawal or two-way flow. In New Zealand, the return line shall comply with the requirements for vapour return and balancing lines. A continuous liquid bypass in the dispenser shall be limited to a flow area of less than 4 mm2. NOTE: Use of bollards or guardrails to protect the dispenser from minor impact is considered good practice but is not mandatory.
Note on H112: 9.3.2 Style A dispenser system Where a Style A dispenser system is required by Figure 9.2, it shall include a dispenser which complies with AS 2229.2/NZS 6109.2 and which is provided with an excess-flow valve, a remote-operated shut-off valve, and a pipe-shear provision, in that order, in all LP Gas pipes attached to the cabinet. The valves shall be below or as close as possible to ground level, with the shear provision above them. Where the remote-operated valve can be relied upon to shut off automatically in the event of pipe shear the excess-flow valve may be omitted. (Additional requirements for service station dispensers are provided in Clause 9.5.16). In addition, the system shall incorporate the following: (a) Control valves The following control valves shall be provided inside the dispenser cabinet and as close as practicable to the flexible hose between the dispenser cabinet and the breakaway coupling: (i) A manually operated positive shut-off valve. (ii) An excess-flow valve. (b) Overspeed sensor A device shall be fitted to the dispensing equipment which has the ability to detect an abnormal flow of fuel, e.g. caused by a hose rupture, and which will shut down the dispenser and the remote pump. (c) Pump control A switch shall be fitted inside the dispensing cabinet which can shut down the remote pump. NOTE: This switching action may be performed automatically by the positioning of the hose nozzle in and out of its receptacle. (d) Return line In Australia, a return line from a dispenser shall comply with the requirements of Table 3.2 for liquid withdrawal or two-way flow. In New Zealand, the return line shall comply with the requirements for vapour return and balancing lines. A continuous liquid bypass in the dispenser shall be limited to a flow area of less than 4 mm2. NOTE: Use of bollards or guardrails to protect the dispenser from minor impact is considered good practice but is not mandatory.
Note on H113: 9.3.2 Style A dispenser system Where a Style A dispenser system is required by Figure 9.2, it shall include a dispenser which complies with AS 2229.2/NZS 6109.2 and which is provided with an excess-flow valve, a remote-operated shut-off valve, and a pipe-shear provision, in that order, in all LP Gas pipes attached to the cabinet. The valves shall be below or as close as possible to ground level, with the shear provision above them. Where the remote-operated valve can be relied upon to shut off automatically in the event of pipe shear the excess-flow valve may be omitted. (Additional requirements for service station dispensers are provided in Clause 9.5.16). In addition, the system shall incorporate the following: (a) Control valves The following control valves shall be provided inside the dispenser cabinet and as close as practicable to the flexible hose between the dispenser cabinet and the breakaway coupling: (i) A manually operated positive shut-off valve. (ii) An excess-flow valve. (b) Overspeed sensor A device shall be fitted to the dispensing equipment which has the ability to detect an abnormal flow of fuel, e.g. caused by a hose rupture, and which will shut down the dispenser and the remote pump. (c) Pump control A switch shall be fitted inside the dispensing cabinet which can shut down the remote pump. NOTE: This switching action may be performed automatically by the positioning of the hose nozzle in and out of its receptacle. (d) Return line In Australia, a return line from a dispenser shall comply with the requirements of Table 3.2 for liquid withdrawal or two-way flow. In New Zealand, the return line shall comply with the requirements for vapour return and balancing lines. A continuous liquid bypass in the dispenser shall be limited to a flow area of less than 4 mm2. NOTE: Use of bollards or guardrails to protect the dispenser from minor impact is considered good practice but is not mandatory.
Note on H114: 9.3.2 Style A dispenser system Where a Style A dispenser system is required by Figure 9.2, it shall include a dispenser which complies with AS 2229.2/NZS 6109.2 and which is provided with an excess-flow valve, a remote-operated shut-off valve, and a pipe-shear provision, in that order, in all LP Gas pipes attached to the cabinet. The valves shall be below or as close as possible to ground level, with the shear provision above them. Where the remote-operated valve can be relied upon to shut off automatically in the event of pipe shear the excess-flow valve may be omitted. (Additional requirements for service station dispensers are provided in Clause 9.5.16). In addition, the system shall incorporate the following: (a) Control valves The following control valves shall be provided inside the dispenser cabinet and as close as practicable to the flexible hose between the dispenser cabinet and the breakaway coupling: (i) A manually operated positive shut-off valve. (ii) An excess-flow valve. (b) Overspeed sensor A device shall be fitted to the dispensing equipment which has the ability to detect an abnormal flow of fuel, e.g. caused by a hose rupture, and which will shut down the dispenser and the remote pump. (c) Pump control A switch shall be fitted inside the dispensing cabinet which can shut down the remote pump. NOTE: This switching action may be performed automatically by the positioning of the hose nozzle in and out of its receptacle. (d) Return line In Australia, a return line from a dispenser shall comply with the requirements of Table 3.2 for liquid withdrawal or two-way flow. In New Zealand, the return line shall comply with the requirements for vapour return and balancing lines. A continuous liquid bypass in the dispenser shall be limited to a flow area of less than 4 mm2. NOTE: Use of bollards or guardrails to protect the dispenser from minor impact is considered good practice but is not mandatory.
Note on H115: 9.3.2 Style A dispenser system Where a Style A dispenser system is required by Figure 9.2, it shall include a dispenser which complies with AS 2229.2/NZS 6109.2 and which is provided with an excess-flow valve, a remote-operated shut-off valve, and a pipe-shear provision, in that order, in all LP Gas pipes attached to the cabinet. The valves shall be below or as close as possible to ground level, with the shear provision above them. Where the remote-operated valve can be relied upon to shut off automatically in the event of pipe shear the excess-flow valve may be omitted. (Additional requirements for service station dispensers are provided in Clause 9.5.16). In addition, the system shall incorporate the following: (a) Control valves The following control valves shall be provided inside the dispenser cabinet and as close as practicable to the flexible hose between the dispenser cabinet and the breakaway coupling: (i) A manually operated positive shut-off valve. (ii) An excess-flow valve. (b) Overspeed sensor A device shall be fitted to the dispensing equipment which has the ability to detect an abnormal flow of fuel, e.g. caused by a hose rupture, and which will shut down the dispenser and the remote pump. (c) Pump control A switch shall be fitted inside the dispensing cabinet which can shut down the remote pump. NOTE: This switching action may be performed automatically by the positioning of the hose nozzle in and out of its receptacle. (d) Return line In Australia, a return line from a dispenser shall comply with the requirements of Table 3.2 for liquid withdrawal or two-way flow. In New Zealand, the return line shall comply with the requirements for vapour return and balancing lines. A continuous liquid bypass in the dispenser shall be limited to a flow area of less than 4 mm2. NOTE: Use of bollards or guardrails to protect the dispenser from minor impact is considered good practice but is not mandatory.
Note on H116: 9.3.3 Dispensing hose The dispensing hose assembly shall comply with Clause 3.6.5 and shall incorporate a selfsealing hose break coupling which complies with the following requirements: (a) The coupling shall disconnect in the event of undue force being applied to the hose, such as a vehicle moving off with the hose connected. NOTE: The coupling should be capable of being re-assembled after separation, preferably without the need for draining the hose, the use of special tools, or the replacement of parts. (b) The force required to separate the coupling shall be less than 600 N for internal hose pressures of 700 kPa to 2500 kPa. (c) The coupling shall retain the liquid within each section of the hose after separation when pressures of 700 kPa to 2500 kPa are maintained in the hose. The volume of liquid lost as a result of parting shall not exceed 15 mL, and the coupling shall not leak after disconnection.
Note on H117: 9.3.4 Dispensing nozzle The dispensing nozzle shall comply with the following requirements: (a) The connection provision shall mate with the filler connection specified in AS/NZS 1425. (b) A provision to start and stop gas flow shall be incorporated and shall be quick-acting (i.e. not a screw-down valve). (c) Where the nozzle is self-sealing, — (i) it shall not be possible to discharge fuel unless the nozzle is connected and fully sealed to the vehicle’s filler connection; (ii) upon disconnection, the amount of liquid released shall not exceed 15 mL. (d) Where a self-sealing nozzle is fitted to a Style A dispenser and is intended for public use, the nozzle lever shall be fitted with a latching device only if one of the following safety features is in place: (i) The nozzle cannot be sufficiently disconnected to cause a leak while the lever is attached. (ii) The dispenser system incorporates an additional device that has to be activated by the person operating the dispenser, and that requires constant actuation by the operator to maintain the flow of fuel. When the device is released, the flow of fuel is stopped. (iii) A device is provided that achieves an equivalent level of safety as Items (i) and (ii) above.
Note on H118: 9.3.4 Dispensing nozzle The dispensing nozzle shall comply with the following requirements: (a) The connection provision shall mate with the filler connection specified in AS/NZS 1425. (b) A provision to start and stop gas flow shall be incorporated and shall be quick-acting (i.e. not a screw-down valve). (c) Where the nozzle is self-sealing, — (i) it shall not be possible to discharge fuel unless the nozzle is connected and fully sealed to the vehicle’s filler connection; (ii) upon disconnection, the amount of liquid released shall not exceed 15 mL. (d) Where a self-sealing nozzle is fitted to a Style A dispenser and is intended for public use, the nozzle lever shall be fitted with a latching device only if one of the following safety features is in place: (i) The nozzle cannot be sufficiently disconnected to cause a leak while the lever is attached. (ii) The dispenser system incorporates an additional device that has to be activated by the person operating the dispenser, and that requires constant actuation by the operator to maintain the flow of fuel. When the device is released, the flow of fuel is stopped. (iii) A device is provided that achieves an equivalent level of safety as Items (i) and (ii) above.
Note on H119: 9.3.5 Filler caps At least two spare standard metal automotive filler caps shall be kept on site for use in the event of a leak at a vehicle-filling connection.
Note on H120: 10.9.5 Use of gloves Protective gloves shall be worn when handling equipment which could involve contact with LP Gas. 10.12.6 Decanting The filling of cylinders by decanting shall be carried out in accordance with Clauses 10.12.1, 10.12.2, 10.12.3 and the following requirements: (a) Protective gloves shall be worn.
Note on H121: D1 TANK SYSTEMS D1.1 Valve indicators and marking A quarter-turn valve shall be provided with indicators and marking in accordance with the following requirements: (a) A means for indicating clearly the open and closed position shall be provided. Where a lever valve is fitted with a fixed handle, the valve shall be open when the handle is in the direction of the pipe. Where a valve handle is removable, a separate metal plate shall be provided, and this plate shall be clearly and indelibly marked to indicate the open and closed positions of the valve. (b) Globe and angle valves shall have handwheels permanently marked with the direction to open. (c) Any valve other than for a safety valve, pressure gauge or fixed liquid level gauge shall be marked to indicate whether it connects to liquid or vapour space. D1.2 Direction of flow A manual isolating valve that is subject to tank pressure shall be installed so that the valve gland is not subject to direct tank pressure when the valve is shut. NOTE: Compliance with this requirement necessitates the mounting of valves in certain locations such as a tank inlet isolating valve contrary to any direction-of-flow marking on the valve. D1.3 Vaporizer marking A vaporizer shall be marked with the following information: (a) Manufacturer’s name or identification mark. (b) The number of the Standard to which the vaporizer is constructed. (c) Design pressure, in kilopascals. (d) Design temperature, in degrees Celsius. (e) The maximum vaporizing capacity in litres per hour. (f) The surface area of the heat exchanger in square metres, as detailed in Paragraph E2 of Appendix E. (g) If direct-fired— (i) the rated input of the heat source; and (ii) the outside surface area of the vaporizer in square metres, as detailed in Paragraph E2, Appendix E.
Note on H122: D2 TANK INSTALLATIONS D2.1 Emergency shut-down system marking Every actuation point for the emergency shutdown system except the provision on the valve itself shall be provided with a sign— (a) marked ‘LP GAS EMERGENCY STOP’ in red letters not less than 40 mm high on a white background; and (b) giving instructions on how to actuate the system, in red or dark lettering not less than 20 mm high on a white or light contrasting background.
Note on H123: D2 TANK INSTALLATIONS D2.2 Tank or tank storage area placarding An above-ground tank or tank storage area shall be provided with a placard in accordance with Paragraph D2.3. Where the tank and pump are underground, the placard shall be in accordance with Figure D1 and Clause 5.3. D2.3 Placard The placard shall display the following information: (a) Phone number of the organization having ownership of the equipment. The nominated phone number shall provide contact with 24-hour specialist advice via the supply company or a contractor. (b) Standard symbols of at least 100 mm diameter for ‘flammable gas’ and ‘no smoking’ or a warning notice in letters not less than 50 mm high prohibiting smoking and ignition sources. Where the area is isolated by a fence, the sign shall be visible from outside the fence and also from points of access. (c) Emergency information panel complying with the requirements of the ADG Code. NOTE: Suitable wording for such signs would be as follows: (i) NO SMOKING, NO FLAME. (ii) NO SMOKING, KEEP FIRE AWAY. (iii) FLAMMABLE GAS, NO SMOKING.
Note on H124: D2 TANK INSTALLATIONS D2.2 Tank or tank storage area placarding An above-ground tank or tank storage area shall be provided with a placard in accordance with Paragraph D2.3. Where the tank and pump are underground, the placard shall be in accordance with Figure D1 and Clause 5.3. D2.3 Placard The placard shall display the following information: (a) Phone number of the organization having ownership of the equipment. The nominated phone number shall provide contact with 24-hour specialist advice via the supply company or a contractor. (b) Standard symbols of at least 100 mm diameter for ‘flammable gas’ and ‘no smoking’ or a warning notice in letters not less than 50 mm high prohibiting smoking and ignition sources. Where the area is isolated by a fence, the sign shall be visible from outside the fence and also from points of access. (c) Emergency information panel complying with the requirements of the ADG Code. NOTE: Suitable wording for such signs would be as follows: (i) NO SMOKING, NO FLAME. (ii) NO SMOKING, KEEP FIRE AWAY. (iii) FLAMMABLE GAS, NO SMOKING.
Note on H125: D2 TANK INSTALLATIONS D2.3 Placard The placard shall display the following information: (a) Phone number of the organization having ownership of the equipment. The nominated phone number shall provide contact with 24-hour specialist advice via the supply company or a contractor. (b) Standard symbols of at least 100 mm diameter for ‘flammable gas’ and ‘no smoking’ or a warning notice in letters not less than 50 mm high prohibiting smoking and ignition sources. Where the area is isolated by a fence, the sign shall be visible from outside the fence and also from points of access. (c) Emergency information panel complying with the requirements of the ADG Code. NOTE: Suitable wording for such signs would be as follows: (i) NO SMOKING, NO FLAME. (ii) NO SMOKING, KEEP FIRE AWAY. (iii) FLAMMABLE GAS, NO SMOKING. D2.4 Construction of signs Signs shall be constructed in accordance with AS 1319. Class labels shall be a minimum of 250 mm square unless permitted to be reduced by the ADG Code.
Note on H126: D4 CYLINDER FILLING D4.1 Decanting cylinder notices The following notices shall be prominently displayed as closely as possible to the decanting point: (a) Standard symbols of at least 100 mm diameter for ‘flammable gas’ and ‘no smoking’ or a warning notice in letters not less than 50 mm high, reading— FLAMMABLE GAS, NO SMOKING (b) Instructions for decanting procedure, including a warning to stop filling as soon as the fixed liquid level gauge indicates that the maximum permitted liquid level has been reached. D4.2 Cylinder filling installations A notice shall be displayed near the cylinder-filling point indicating ‘NO SMOKING, NO FLAME’ in letters not less than 50 mm high.
Note on H128: 9.5.14 Remote shut-down system A remote shut-down system shall be fitted and shall be as follows: (a) Capable of initiation at the following locations as a minimum, with at least one actuation point being accessible at all hours: (i) Within 10 m from the tank filling point. (ii) For self-service sites, at a point easily accessible and visible from the console. (iii) For attendant-operated sites, either at the dispenser or at a point which is easily accessible to the attendant. (iv) At a remote location external to any building and distant from the tank filling point and console, in a direction to allow ready egress from the site. (b) Of a fail-safe design which will close all liquid supply, pump bypass and vapour return tank connections and shut down the pump systems as quickly as possible with a response time of no more than 10 s when operated from any point. (c) Checked in accordance with the requirements of the site safety management system (see Clause 9.8) with test results recorded and the records retained on site. If any defect compromising safety is identified, the tank shall be manually isolated until such time as the system is returned to full function. (d) Designed and installed so that manual action is required to re-open the valves to resume operation. (e) Designed and installed so that it achieves a high degree of reliability. (f) Provided with instructions on how to actuate it and marked in accordance with Paragraph D2.1(a). (g) Provided with clear access to the actuation points and with such access being maintained. NOTE: The remote shutdown system and the emergency shutdown system (see Clause 4.8) may use common componentry provided the function of each system is satisfied.
Note on H129: 9.2.1 Ignition sources The design of the installation shall be such that ignition sources are not located in and are not permitted in a hazardous area as described in the relevant Parts of AS/NZS 2430 (see Clause 1.4.28). A vehicle is not regarded as being an ignition source while it is entering or leaving the hazardous zone surrounding a LP Gas dispenser or a bulk LP Gas filling connection. However, it is treated as a potential ignition source during the period of bulk liquid transfer, and precautionary measures need to be taken (see Clause 10.11).
Note on H130: 9.8 SAFETY MANAGEMENT SYSTEM A safety management system shall be prepared and implemented. Compliance with the ALPGA publication LP Gas Automotive Retail Outlets––Code of Practice for Safe Operation is deemed to constitute a means of compliance with this requirement and Clause 10.2.
Note on H132: 10.3.4 Operating procedures The operating procedures shall be appropriate to the particular installation and shall take into account, amongst other things, the following: (a) Identification of safe areas. (b) Initial commissioning procedures. (c) Normal handling procedures. (d) Monitoring of essential functions and equipment. (e) Recognition of fault conditions. (f) Product transfer. (g) Housekeeping and site upkeep. (h) Any manufacturer’s operating instructions for equipment. (i) Equipment not in use (i.e. isolation, deactivation, identification). (j) Maintaining clear spaces for access. (k) Personnel safety. (l) Personal protective equipment. (m) Control of ignition sources. (n) Earthing and bonding. (o) Control of access, security and lock-up. (p) Vehicle movement.
Note on H133: 10.3.5 Construction and maintenance procedures The construction and maintenance procedures shall be appropriate to the particular installation and shall take into account, amongst other things, the following: (a) Periodic testing of protective devices, alarms, and personal protective equipment. (b) Regular testing of hoses. (c) Establishment of safe areas. (d) LP Gas purging. (e) Isolation and tagging. (f) Control of contractors. (g) Work authorization. (h) Confined spaces. (i) Hot work permits (j) Firefighting equipment. (k) Pipelines and equipment. (l) Storage tanks. (m) Electrical equipment. (n) Fences and security measures, signs, notices. (o) Lighting. (p) The needs of any other individual item or plant components, e.g. pumps, equipment.
Note on H134: 10.3.6 Emergency procedures The emergency procedures shall be appropriate to the particular installation and shall take into account, amongst other things, the following: (a) List of contacts, emergency services, phone numbers. (b) Chain of command. (c) List of duties. (d) Any mutual aid (inter-company) arrangements. (e) Cooperation with relevant authorities, and compatibility with equipment. (f) Fire teams (initial response). (g) Fire drills. (h) Evacuation provisions. (i) Assembly points. (j) First aid. (k) Debriefing and reporting. (l) Vehicles on site. (m) Contractors. (n) Access control. (o) Site plan. For large sites storing dangerous goods in addition to LP Gas the total site shall be considered when preparing on-site and off-site emergency plans. NOTE: Appendix M provides relevant information on on-site and off-site emergency plans.
Note on H135: 10.3.7.1 Employees Each employee shall be trained in such duties as have been individually assigned to that person in connection with LP Gas. In addition, the training shall include the following, as appropriate: (a) Procedures to be followed in the event of an incident (accident, fire). (b) Layout of the installation. (c) Location of firefighting equipment. (d) Basic principles of first aid firefighting, and the use of fire hose reels and fireextinguishers. (e) Regulations relevant to the employee’s tasks. (f) Properties, characteristics and hazards of any materials kept or handled. (g) Correct use of any personal protective equipment provided. (h) Area housekeeping. NOTE: Procedures and precautions for motor vehicle refuelling are provided in Appendix N.
Note on H136: 10.3.7.2 Contractors Contractors and their staff shall be trained in the following as appropriate to the site: (a) Properties, characteristics and hazards of any materials likely to be encountered and appropriate for the site. (b) Correct use of any necessary personal protective equipment provided. (c) Hazards likely to be encountered. (d) Procedures to be followed in the event of an incident (spillage, accident, fire). (e) Layout of the installation. (f) Location of firefighting equipment. (g) Basic principles of first aid firefighting, and the use of fire hose reels and fire extinguishers. (h) Any regulations relevant to their tasks. (i) Area housekeeping. (j) Safety rules of the installation. (k) Conditions and obligations associated with work permits and confined-space entry permits.
Note on H137: 10.4.2 Supervision All operational and maintenance work shall be planned and supervised. All necessary precautions shall be observed. 10.4.3 Records Records shall be kept of the following: (a) Training and retraining (permanent record). (b) Routine testing of safety equipment and fire protection equipment (as required by this Standard and other referenced Standards). (c) In-service inspections (life of installation). (d) Training drills (six years). (e) Maintenance and repairs, and equipment deficiencies (life of equipment). (f) Abnormal incidents, including ‘near-miss’ occurrences (life of installation). The suggested periods for retention of records are indicated in parenthesis.
Note on H138: 10.5 CONSTRUCTION, INSPECTION, TESTING AND MAINTENANCE 10.5.1 Installation certification Before an installation is put into service, it shall be certified in writing that the complete installation was installed, tested and proved to be leak-free and in accordance with the installation specifications and the provisions of this Standard. 10.5.2 Scheduled checks A routine check procedure shall be prepared for each installation appropriate to that installation. Such a procedure shall cover all operating valves and systems, instruments, emergency shut-down systems, safety valve protective caps and discharge provisions, and fire protection equipment. Tank-emptying provisions are excluded. In particular, emergency shut-off valves shall be operated at intervals not exceeding 1 month, from each available operation point. A pumping and supplementary fire protection system shall be tested in accordance with the relevant Parts of AS 1851. A record of tests and inspections shall be kept. NOTE: Where an emergency system installation can be actuated from any of a number of points, it is not necessary to test all such points on the same day, i.e. operation may be tested from the various points in rotation, provided that each has been checked within the stated time. 10.5.3 Tanks Tanks shall be inspected according to regulatory requirements. The following additional requirements apply to underground tanks: (a) Where tests prove the effectiveness of the corrosion-resistant system, periodic external inspection of a tank need not be made. Inspection of test plates or probes buried close to a tank and connected to it may be used as evidence of satisfactory cathodic protection. (b) Tanks shall be inspected at the end of the effective life of sacrificial anodes or when tests indicate the permanent loss of effectiveness of the cathodic protection system or coating. (c) When any fault is found in the protective coating, it shall be stripped in the immediate vicinity of the fault and the underlying metal surface examined. Such defective coating shall be repaired and tested to ensure compliance with Clause 5.2. (d) Cathodic protection systems shall be tested at intervals not exceeding 6 months and record of these tests shall be kept and shall be available for 10 years. NOTE: AS 2832.2 provides guidelines for operation and maintenance of cathodic protection systems. 10.5.4 Piping Piping for LP Gas, whether it is new, modified, or added piping, shall be tested in accordance with the relevant procedures detailed in Appendix H. 10.5.5 Hoses Transfer hoses other than decanting hoses shall be periodically inspected and tested as follows: (a) Visually inspected for damage over the whole length in use at intervals not exceeding 1 month. (b) Hoses and couplings which are assembled and tested in accordance with the manufacturers’ guidelines, and in compliance with AS/NZS 1869, shall, at the end of five years’ service, be either–– (i) replaced; or (ii) tested at a pressure of 2.4 MPa at intervals not exceeding one year thereafter. (c) Electrical continuity check of hoses containing electrical continuous wiring at intervals not exceeding 1 year in accordance with AS/NZS 1869. Delivery hose for in-situ filling shall be inspected visually over its entire length weekly. Hoses which fail inspection or testing shall be discarded or repaired. 10.5.6 Flexible connections Metal flexible connections shall be inspected visually at intervals not exceeding 1 year and shall be hydrostatically tested to 3.6 MPa at intervals not exceeding 5 years. Elastomeric flexible connections shall be inspected and tested as for transfer hose. Metal flexible connections which fail inspection or test shall be replaced. 10.5.7 Protective flow-control valves Excess-flow valves and non-return valves shall be checked immediately after installation to ensure correct functioning. Hydrostatic relief valves shall be checked in accordance with AS/NZS 3788. NOTE: AS/NZS 3788 requires that pressure relief valves for LP Gas be tested at intervals not exceeding the internal inspection interval for the vessel, provided that weatherproof external protection prevents dust, rain or other contamination from affecting the valve’s performance. 10.5.8 Authorization of work No work shall be carried out on any LP Gas installation without authorization in one of the following forms: (a) A verbal instruction, which shall be limited to non-hazardous actions or to work for which the person has been trained. (b) Procedures in accordance with Clause 10.5.10 for which the person has been trained. 10.5.9 Safe procedures Work on or near any components containing LP Gas shall be undertaken only after necessary steps have been taken to ensure safety. Safe work procedures shall be followed. These may be in the form of compliance with the following: (a) AS/NZS 2865. (b) A recognized safe work system. (c) A recognized work permit system including a hot work permit in accordance with AS 1674.1. (d) Clause 10.5.10. 10.5.10 Work preparation Appropriate procedures shall be adopted and responsibilities assigned to ensure that the relevant site area and plant are properly prepared to prevent injury to people, damage, fire or explosion. Particular attention shall be paid to the following, as appropriate: (a) Observance of any written safety procedures. (b) Liaison with site operator. (c) Testing for flammable gas and oxygen levels, particularly for any confined spaces, pits, trenches and other potentially hazardous areas. (d) Removal of protective devices unless substitute protection has been provided. (e) Prevention of inadvertent operation during maintenance.(f) Prevention of contamination of equipment by water, dirt, foreign matter, or other materials. (g) Identification of both the equipment to be worked on and all other equipment affected, including underground piping or equipment. (h) Depressurization and disconnection. (i) Isolation from other equipment. (j) Blanking or capping opened connections. (k) Purging of the equipment. (l) Removal of combustible materials. (m) Sealing off of sewers, drains and gutters. (n) Provision of additional protection, fireguards, and firefighting equipment. (o) Tagging where required. 10.5.11 Completion of work Upon completion of work, a check shall be made to ensure that— (a) any written safety procedures have been followed; (b) the work has, in fact, been completed; (c) any temporary arrangements have been discontinued, e.g. bypass lines or blank flanges have been removed or fuses replaced; (d) all personnel and equipment are accounted for; (e) relevant work permits or other documentation have been signed off; and (f) the site operator is notified of status. 10.5.12 Site upkeep The area around any storage and handling facility and the installation itself shall be maintained in a safe condition. In particular–– (a) any accumulation of flammable or combustible materials, of a type and quantity sufficient to constitute a significant heat radiation hazard to the installation in the event of fire in those materials, shall be removed; (b) specified clearance distances shall be maintained; (c) vegetation that could become a fire hazard shall be kept short; (d) the area shall be kept clear of all extraneous material; (e) lighting shall be kept operational and effective; (f) the surface coating of any tanks shall be maintained in good condition; and (g) signs and notices shall be legible.
Note on H139: 10.6.1 Commissioning new or modified equipment No installation or part thereof shall be brought into service until operating and emergency procedures and associated equipment are available, appropriate to the facility being brought into service, and adequate personnel are available to cope with any likely fault condition.
Note on H142: 2.1 BASIC REQUIREMENTS AND RECOMMENDATION Pressure equipment covered by this Standard and used or intended for use in Australia or New Zealand— (a) shall comply with the construction and use requirements specified in the Standards listed in Table 2.1 or equivalent agreed by the parties concerned; NOTE: See Figure G1 in Appendix G for organization of Australian, New Zealand and other pressure equipment Standards. (b) shall comply with applicable legislative or regulatory requirements; (c) shall comply with applicable contractual requirements; and (d) should comply with the safety recommendations given in Appendix J. 2.2 COMPLIANCE STANDARDS Compliance with the applicable Standards listed in Table 2.1 is deemed to satisfy Clause 2.1(a) and (d). Where a Standard is used, that Standard and all its referenced Standards shall be as referenced in their entirety, except as provided by Clause 2.3. Published application Standards should be viewed only as a starting point in the control of risks. It should not be assumed that a design that meets the Standard is without risk. This is because the Standard itself may not deal with all the matters relevant to hazard identification, risk assessment and risk control for the plant in question. Appropriate judgement needs to be exercised in such circumstances. Designers, when designing plant to specifications in published application Standard(s), such as those listed in Table 2.1, shall determine whether the Standard(s) fully deals with the risk to health or safety identified in the risk assessment process. This should involve a systematic assessment of whether the application Standard(s) apply to the whole plant or only certain parts of the plant and an assessment of the adequacy of the Standard(s) in controlling a particular type of risk, having regard to the state of knowledge. If designing the plant in accordance with application Standard(s) listed in Table 2.1, or any other published application Standard, does not eliminate the risk to health or safety, the designer is required to reduce the risk so far as is practicable by altering the design of the plant. If the redesign still does not adequately control the risk, the designer is required to specify the risk control measures that require implementation when the plant is used. 2.3 MIXING STANDARDS Pressure equipment shall comply with the full requirements of a Standard, except when the equipment or parts of the equipment comply with the more appropriate requirements of other pressure equipment Standards provided— (a) such Standards comply with an agreed alternative or equivalent and are applicable to the particular pressure equipment; (b) the relevant requirements of the Standards apply to the parts concerned; (c) at the interfaces between the parts with different Standards, the parts comply with both Standards as appropriate; (d) the design data, drawings and manufacturer’s data report clearly identify and record departures from the principal Standard; (e) the equipment marking includes the two main Standards used; (f) the overall equipment complies with Clause 2.1; and
Note on H149: Available from Sept 2007
Note on H150: Available from 2007
Note on H151: Available from 2007
Note on H152: Available from 2007
Note on H153: Available from 2007
Note on H155: Available from 2007
Note on H156: Available from 2007
Note on H157: Available from 2007
Note on H158: Available from 2007
Note on H159: Available from 2007
Note on H160: Available from 2007
Note on H161: Available from 2007
Note on H162: Available from 2007
Note on H163: Available from 2007
Note on H164: Available from 2007
Note on H165: Available from 2007
Note on H166: Available from 2007